## YourData
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  |  | Sec5-2Aout.xlsx |  | 2020-01-01
Output Spreadsheet for Standard 140 Building Thermal Fabric Modeling Comparative Test Cases of Sections 5.2.1, 5.2.2, and 5.2.3
[Note to Users: This file is reorganized since 140-2017. Red text indicates content changes to 140-2017.]
INSTRUCTIONS:
1. Use specified units.
2. All solar radiation data is for sum of direct and diffuse solar radiation.
3. Output terminology is defined in Section 6.2.1
4. Format dates using the appropriate three-character month code,
one- or two-digit day, and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 8th hour interval (0700-0800),
shall be input as:
Month | Day | Hour
Jan | 4 | 8
5. Data entry is restricted to the following ranges:
| C61…C63: | Software Name, Version, and Date of Results
| C70…L115: | Conditioned Zone Loads (Non-Free-Float Test Cases)
| C130…K136: | Free-Float Case Zone Temperatures
| C155…C171: | Solar Radiation, as specified
| C178…K178: | Sky Temperature
| C190…R201: | Monthly Conditioned Zone Loads (Cases 600 and 900)
| C230…T253: | Specific-Day Hourly Output: incident and transmitted solar radiation and sky temperatures
| C262…Z285: | Specific-Day Hourly Output: zone loads (selected cases) and conditioned-zone temperatures (Cases 640 and 940)
| C294…H317: | Specific-Day Hourly Output: free float temperatures
| C330…C478: | Case 900FF Zone Temperature Bin Data, enter 8760 hours of zone temperature data in
Sheet 'TMPBIN' (next tab), as specified in Cell E1 there. Bin data will flow to C330 - C478
on this sheet (sheet 'A').
| USER NOTE: Paste new data in row 61 and below. | Program Label in C61 flows to data labels in charts and figures. Avoid overwrite or re-enter "='Adding Results'!G24" there.
Version and Date of Results will also transfer from 'Adding Results' sheet.
To print pdf file, see instructions on "Title Page" tab.
Enter identifying information in C61, C62, C63
| Software: | EnergyPlus
| Version: | Version 9.0.1
| Date of Results: | 2018-10-19
Conditioned Zone Loads (Non-Free-Float Test Cases)
|  | ANNUAL LOADS |  |  |  | ANNUAL HOURLY INTEGRATED PEAK LOADS
|  | Heating | Cooling | Heating |  |  |  | Cooling
| CASE# | MWh | MWh | kW | Month* | Day | Hour | kW | Month* | Day | Hour
| 600 | 4.324 | 6.027 | 3.204 | Dec | 31 | 24 | 6.352 | Jan | 22 | 14
| 610 | 4.375 | 4.333 | 3.192 | Dec | 31 | 24 | 6.135 | Dec | 1 | 14
| 620 | 4.485 | 4.06 | 3.229 | Dec | 31 | 24 | 4.797 | Jun | 26 | 17
| 630 | 4.784 | 2.836 | 3.207 | Dec | 31 | 24 | 4.212 | Jun | 26 | 17
| 640 | 2.662 | 5.763 | 4.559 | Nov | 26 | 8 | 6.297 | Jan | 22 | 14
| 650 | 0 | 4.817 | 0 | Jan | 1 | 1 | 6.138 | Oct | 18 | 14
| 660 | 3.707 | 3.232 | 2.831 | Dec | 31 | 24 | 3.77 | Oct | 18 | 14
| 670 | 5.616 | 6.623 | 3.854 | Nov | 26 | 7 | 6.806 | Jan | 22 | 14
| 680 | 2.18 | 6.444 | 2.052 | Nov | 26 | 7 | 6.77 | Jan | 22 | 14
| 685 | 4.877 | 9.119 | 3.223 | Dec | 31 | 24 | 7.107 | Jan | 22 | 14
| 695 | 2.802 | 9.172 | 2.072 | Dec | 31 | 24 | 7.334 | Jan | 22 | 14
| 900 | 1.664 | 2.489 | 2.687 | Feb | 9 | 6 | 3.04 | Oct | 1 | 14
| 910 | 1.956 | 1.383 | 2.699 | Feb | 9 | 6 | 2.222 | Oct | 18 | 15
| 920 | 3.337 | 2.731 | 2.77 | Feb | 9 | 6 | 3.26 | Jun | 26 | 18
| 930 | 3.994 | 1.919 | 2.785 | Feb | 9 | 6 | 2.782 | Jun | 26 | 18
| 940 | 1.067 | 2.424 | 3.143 | Dec | 31 | 9 | 3.04 | Oct | 1 | 14
| 950 | 0 | 0.707 | 0 | Jan | 1 | 1 | 2.388 | Sep | 11 | 15
| 960 | 2.689 | 0.907 | 2.259 | Feb | 9 | 6 | 1.48 | Jun | 26 | 17
| 980 | 0.411 | 3.712 | 1.538 | Feb | 9 | 6 | 3.45 | Oct | 18 | 15
| 985 | 2.369 | 6.359 | 2.695 | Feb | 9 | 6 | 3.915 | Oct | 18 | 15
| 995 | 1.006 | 7.203 | 1.622 | Feb | 9 | 6 | 4.177 | Jan | 22 | 15
| 195 | 4.07 | 0.612 | 1.794 | Dec | 31 | 24 | 1.041 | Jun | 26 | 17
| 200 | 5.105 | 0.814 | 2.341 | Nov | 26 | 8 | 1.307 | Jun | 26 | 17
| 210 | 6.047 | 0.56 | 2.565 | Dec | 31 | 24 | 1.084 | Jun | 26 | 17
| 215 | 5.405 | 0.877 | 2.478 | Nov | 26 | 8 | 1.4 | Jun | 26 | 17
| 220 | 6.455 | 0.61 | 2.692 | Dec | 31 | 24 | 1.184 | Jun | 26 | 18
| 230 | 9.93 | 0.991 | 4.316 | Dec | 31 | 24 | 1.841 | Jun | 26 | 17
| 240 | 5.279 | 0.979 | 2.507 | Dec | 31 | 24 | 1.366 | Jun | 26 | 18
| 250 | 4.899 | 3.182 | 2.687 | Dec | 31 | 24 | 2.867 | Sep | 12 | 14
| 270 | 4.385 | 7.522 | 2.597 | Dec | 31 | 24 | 6.839 | Jan | 22 | 14
| 280 | 4.57 | 5.183 | 2.602 | Dec | 31 | 24 | 4.727 | Jan | 22 | 14
| 290 | 4.424 | 5.743 | 2.583 | Dec | 31 | 24 | 6.595 | Jan | 22 | 14
| 300 | 4.425 | 5.152 | 2.603 | Dec | 31 | 24 | 4.475 | Jun | 26 | 17
| 310 | 4.691 | 3.669 | 2.58 | Dec | 31 | 24 | 3.97 | Jun | 26 | 18
| 320 | 3.771 | 4.986 | 2.573 | Dec | 31 | 24 | 6.209 | Jan | 22 | 14
| 395 | 4.641 | 0.01 | 1.952 | Dec | 31 | 24 | 0.377 | Jun | 26 | 19
| 400 | 6.348 | 0.031 | 2.692 | Dec | 31 | 24 | 0.607 | Jun | 26 | 18
| 410 | 8.08 | 0.057 | 3.504 | Dec | 31 | 24 | 0.828 | Jun | 26 | 18
| 420 | 6.906 | 0.153 | 3.319 | Dec | 31 | 24 | 1.033 | Jun | 26 | 18
| 430 | 5.62 | 0.856 | 3.316 | Dec | 31 | 24 | 1.929 | Jun | 26 | 16
| 440 | 4.5 | 4.085 | 3.219 | Dec | 31 | 24 | 4.686 | Oct | 18 | 14
| 450 | 3.962 | 6.507 | 3.1 | Dec | 31 | 24 | 6.466 | Jan | 22 | 14
| 460 | 4.194 | 6.475 | 3.091 | Dec | 31 | 24 | 6.374 | Jan | 22 | 14
| 470 | 4.094 | 6.029 | 3.207 | Dec | 31 | 24 | 6.444 | Jan | 22 | 14
| 800 | 5.116 | 0.374 | 2.924 | Feb | 9 | 6 | 1.046 | Jun | 26 | 16
| 810 | 2.342 | 1.508 | 2.749 | Feb | 9 | 6 | 2.27 | Sep | 11 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
Free-Float Case Zone Temperatures
|  | Ann. Hourly |  | Annual Hourly Integrated Zone Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600FF | 24.92 | -12.56 | Feb | 9 | 7 | 63.84 | Oct | 18 | 16
| 900FF | 25.12 | 1.24 | Feb | 9 | 7 | 44.29 | Sep | 12 | 15
| 650FF | 18.42 | -17.08 | Dec | 31 | 24 | 62.47 | Oct | 18 | 16
| 950FF | 14.79 | -12.81 | Feb | 9 | 7 | 36.68 | Sep | 11 | 16
| 680FF | 30.96 | -7.05 | Feb | 9 | 7 | 70.14 | Jan | 22 | 16
| 980FF | 31.16 | 9.92 | Nov | 4 | 7 | 49.62 | Sep | 12 | 16
| 960 | 27.74 | 5.09 | Feb | 9 | 7 | 49.88 | Oct | 12 | 15
* Apply month abbreviations of cells C19 to C30 as appropriate.
SOLAR RADIATION
(USE COLUMN B ONLY)
ANNUAL INCIDENT (Total Direct-Beam and Diffuse)
CASE 600
| Surface | kWh/m2
| HORZ. | 1664.34
| NORTH | 438.24
| EAST | 1062.16
| SOUTH | 1370.48
| WEST | 967.28
UNSHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 600/South | 804.02
| 660/South | 436
| 670/South | 1024.2
| 620/West | 581.04
SHADED ANNUAL TRANSMITTED (Total Direct-Beam and Diffuse)
| Case/Surf. | kWh/m2
| 610/South | 646.13
| 630/West | 419.35
Sky Temperature Output
|  | Ann. Hourly |  | Annual Hourly Integrated Sky Temperature Extremes
|  | Average | Minimum |  |  |  | Maximum
| CASE# | °C | °C | Month* | Day | Hour | °C | Month* | Day | Hour
| 600 | -2.02 | -37.98 | Dec | 31 | 24 | 24.73 | Aug | 4 | 16
* Apply month abbreviations of cells C19 to C30 as appropriate.
Monthly Conditioned Zone Loads (Cases 600 and 900)
[5 empty] | Case 600 | [7 empty] | Case 900
|  | Total | Total |  | Hourly Integrated Peak Loads |  |  |  |  | Total | Total |  | Hourly Integrated Peak Loads
|  | Heating | Cooling | Peak Heating |  |  | Peak Cooling |  |  | Heating | Cooling | Peak Heating |  |  | Peak Cooling
| Month | kWh | kWh | kW | Day | Hour | kW | Day | Hour | kWh | kWh | kW | Day | Hour | kW | Day | Hour
| Jan | 711.88 | 521.8 | 2.978 | 1 | 3 | 6.352 | 22 | 14 | 255.84 | 53.28 | 1.903 | 29 | 7 | 2.078 | 22 | 15
| Feb | 682.63 | 387.5 | 3.067 | 9 | 6 | 5.537 | 2 | 14 | 294.18 | 12.34 | 2.687 | 9 | 6 | 0.979 | 15 | 15
| Mar | 472.22 | 484.36 | 2.115 | 17 | 6 | 5.009 | 9 | 14 | 125.54 | 65.39 | 1.744 | 17 | 6 | 1.493 | 11 | 14
| Apr | 510.12 | 240.46 | 2.322 | 11 | 5 | 3.931 | 12 | 14 | 268.65 | 18.47 | 2.004 | 3 | 4 | 0.953 | 7 | 15
| May | 136.82 | 339.91 | 1.624 | 1 | 5 | 3.086 | 10 | 13 | 33.41 | 114.49 | 1.268 | 1 | 5 | 1.534 | 11 | 14
| Jun | 10.08 | 539.6 | 0.732 | 9 | 5 | 3.449 | 13 | 13 | 0 | 401.33 | 0 | 1 | 1 | 1.966 | 14 | 14
| Jul | 12.02 | 536.38 | 0.514 | 26 | 5 | 3.628 | 17 | 14 | 0 | 398.71 | 0 | 1 | 1 | 2.068 | 17 | 15
| Aug | 6.59 | 648.5 | 0.479 | 17 | 6 | 4.672 | 26 | 14 | 0 | 510.32 | 0 | 1 | 1 | 2.526 | 29 | 15
| Sep | 73.32 | 733.71 | 1.13 | 28 | 24 | 5.715 | 30 | 13 | 0.11 | 492.84 | 0.064 | 29 | 7 | 2.989 | 11 | 15
| Oct | 347.71 | 675.27 | 1.682 | 15 | 5 | 6.222 | 18 | 14 | 81.09 | 292.67 | 1.326 | 7 | 7 | 3.04 | 1 | 14
| Nov | 625.26 | 437.68 | 3.106 | 26 | 7 | 6.194 | 28 | 13 | 296.99 | 67.98 | 2.316 | 26 | 7 | 2.002 | 20 | 15
| Dec | 735.73 | 481.86 | 3.204 | 31 | 24 | 6.251 | 1 | 14 | 307.87 | 60.94 | 2.175 | 31 | 7 | 1.968 | 2 | 15
Specific-Day Hourly Output (Hourly Integrated Values)
|  | Incident Solar Radiation (Total Direct-Beam and Diffuse) | [6 empty] | Sky Temperature |  |  |  | Transmitted Total* Solar Radiation
|  |  | Case 600, May 4 (Cloudy) |  |  | Case 600, July 14 (Clear) |  | Feb 1 | May 4 | July 14 | Feb 1 (Clear/Cold) |  |  | May 4 (Cloudy) |  |  | July 14 (Clear/Hot)
| Surf. or Case | Horizontal | South | West | Horizontal | South | West | 600 | 600 | 600 | 600 | 660 | 670 | 600 | 660 | 670 | 600 | 660 | 670
| HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | °C | °C | °C | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | -22.97 | -1.17 | 4.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | 0 | 0 | 0 | 0 | 0 | 0 | -24.14 | -1.19 | 3.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | -25.32 | -1.26 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | -27.19 | -1.44 | 1.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 5.65 | 2.83 | 2.83 | -26.9 | -1.44 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 0.92 | 2.13
| 6 | 21.25 | 10.98 | 10.98 | 103.19 | 27.06 | 27.06 | -26.67 | -1.44 | 1.79 | 0 | 0 | 0 | 6.55 | 3.56 | 8.27 | 16.14 | 8.78 | 20.38
| 7 | 64.75 | 33.82 | 33.82 | 289.86 | 55.39 | 55.39 | -27.39 | -1.19 | 4.42 | 0 | 0 | 0 | 20.17 | 10.98 | 25.47 | 33.03 | 17.97 | 41.71
| 8 | 114.58 | 59.97 | 59.78 | 493.43 | 82.4 | 81.97 | -26.6 | -0.88 | 6.6 | 109.56 | 58.7 | 144.96 | 35.76 | 19.46 | 45.16 | 48.9 | 26.61 | 61.75
| 9 | 160.25 | 84.39 | 83.07 | 682.34 | 179.12 | 104.12 | -25.36 | -0.53 | 8.39 | 323.8 | 175.19 | 408.87 | 50.33 | 27.39 | 63.55 | 70.5 | 38.63 | 96.5
| 10 | 203.25 | 108.11 | 104.63 | 837.84 | 305.79 | 119.48 | -24.49 | 0.65 | 10.71 | 484.08 | 263.02 | 596.1 | 64.48 | 35.08 | 81.42 | 116.64 | 63.03 | 170.68
| 11 | 259.83 | 139.61 | 132.04 | 948 | 396.71 | 128.25 | -23.15 | 1.86 | 12.61 | 591.94 | 322.57 | 720.94 | 83.26 | 45.3 | 105.13 | 169.45 | 90.48 | 244.31
| 12 | 276.58 | 149.44 | 140.24 | 1005.24 | 443.51 | 131.55 | -21.79 | 2.1 | 13.27 | 648.74 | 354.51 | 786.61 | 89.13 | 48.49 | 112.54 | 201.82 | 107.48 | 286.21
| 13 | 274.08 | 147.92 | 142.63 | 1004.03 | 442.66 | 258.93 | -20.21 | 0.88 | 13.9 | 654.84 | 357.98 | 793.67 | 88.22 | 48 | 111.4 | 201.24 | 107.17 | 285.47
| 14 | 255.17 | 136.71 | 137.73 | 946.15 | 394.89 | 491.65 | -20.69 | -0.55 | 14.39 | 609.27 | 332.27 | 740.93 | 81.54 | 44.36 | 102.95 | 168.17 | 89.81 | 242.66
| 15 | 222 | 117.61 | 123.31 | 835.48 | 303.17 | 683.86 | -21.77 | -2.04 | 14.9 | 513.04 | 278.94 | 629.54 | 70.14 | 38.16 | 88.57 | 115.27 | 62.32 | 168.67
| 16 | 172 | 90 | 96.87 | 679.26 | 175.53 | 811.98 | -22.21 | -2 | 14.78 | 366.66 | 198.67 | 459.36 | 53.68 | 29.21 | 67.78 | 69.61 | 38.14 | 94.97
| 17 | 101.92 | 53.26 | 54.93 | 489.97 | 81.51 | 853.44 | -22.93 | -1.83 | 14.47 | 178.37 | 95.79 | 233.51 | 31.77 | 17.28 | 40.11 | 48.62 | 26.45 | 61.39
| 18 | 50.25 | 26.16 | 26.16 | 285.84 | 54.81 | 778.08 | -24.62 | -2.11 | 13.6 | 9.79 | 5.2 | 13.56 | 15.61 | 8.49 | 19.7 | 32.69 | 17.79 | 41.27
| 19 | 10.53 | 5.43 | 5.43 | 99.08 | 26.26 | 527.4 | -25.92 | -2.36 | 12.31 | 0 | 0 | 0 | 3.24 | 1.76 | 4.09 | 15.66 | 8.52 | 19.78
| 20 | 0 | 0 | 0 | 4.44 | 2.35 | 70.21 | -26.5 | -2.94 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0.76 | 1.77
| 21 | 0 | 0 | 0 | 0 | 0 | 0 | -27.61 | -3.22 | 9.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 22 | 0 | 0 | 0 | 0 | 0 | 0 | -28.94 | -3.75 | 7.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 23 | 0 | 0 | 0 | 0 | 0 | 0 | -29.44 | -4.79 | 7.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24 | 0 | 0 | 0 | 0 | 0 | 0 | -29.27 | -5.26 | 5.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Direct-Beam and Diffuse
| Specific-Day Hourly Output (Continued) (Hourly Integrated Values) | [22 empty] | Conditioned Zone
|  | Zone Loads** | [13 empty] | Zone Loads** | [7 empty] | Temperatures
|  | Feb 1 (Clear/Cold) | [11 empty] | July 14 (Clear/Hot) | [9 empty] | Feb 1 (Clear/Cold)
| Surf. or Case | 600 | 640 | 660 | 670 | 680 | 685 | 695 | 900 | 940 | 980 | 985 | 995 | 600 | 660 | 670 | 680 | 685 | 695 | 900 | 980 | 985 | 995 | 640 | 940
| HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | °C | °C
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
[5 empty] | ** Use "-" (minus sign) for cooling | [10 empty] | ** Use "-" (minus sign) for cooling
Specific-Day Hourly Output (Continued) (Hourly Integrated Values)
Free Float Zone Temperatures
|  | Feb 1 (Clear/Cold) |  | July 14 (Clear/Hot) |  | Feb 1 (Clear/Cold)
| Surf. or Case | 600FF | 900FF | 650FF | 950FF | 680FF | 980FF
| HOUR | °C | °C | °C | °C | °C | °C
| 1 | 5.44 | 12.94 | 19.87 | 21.23 | 15.35 | 22.75
| 2 | 3.81 | 12.43 | 19.06 | 20.72 | 13.48 | 22.24
| 3 | 2.37 | 11.93 | 18.14 | 20.03 | 11.78 | 21.76
| 4 | 1.09 | 11.43 | 17.02 | 19.16 | 10.19 | 21.28
| 5 | -0.01 | 10.99 | 15.88 | 18.25 | 8.78 | 20.86
| 6 | -0.9 | 10.58 | 16.39 | 18.63 | 7.51 | 20.46
| 7 | -1.71 | 10.17 | 18.76 | 20.27 | 6.35 | 20.08
| 8 | -1.48 | 10.32 | 20.89 | 22.87 | 6.29 | 20.25
| 9 | 2.71 | 11.75 | 23.3 | 24.4 | 10.04 | 21.66
| 10 | 9.93 | 13.81 | 26.43 | 25.57 | 16.59 | 23.55
| 11 | 18.73 | 15.96 | 30.62 | 26.91 | 24.7 | 25.59
| 12 | 28.01 | 18.21 | 35.22 | 28.18 | 33.65 | 27.79
| 13 | 36.57 | 20.44 | 39.19 | 29.13 | 42.51 | 29.97
| 14 | 43.39 | 22.01 | 42.1 | 29.86 | 49.77 | 31.47
| 15 | 46.98 | 22.72 | 44.21 | 30.29 | 54.39 | 32.08
| 16 | 47.59 | 22.82 | 44.89 | 30.43 | 56.31 | 32.2
| 17 | 44.88 | 22.1 | 44.6 | 30.43 | 54.98 | 31.46
| 18 | 38.7 | 20.49 | 43.74 | 30.35 | 50.21 | 29.83
| 19 | 32.16 | 19.22 | 34.48 | 29.03 | 44.93 | 28.67
| 20 | 26.3 | 18.32 | 30.86 | 27.65 | 39.97 | 27.86
| 21 | 21.53 | 17.54 | 27.96 | 26.34 | 35.6 | 27.16
| 22 | 17.03 | 16.76 | 25.99 | 25.53 | 31.65 | 26.49
| 23 | 13.28 | 15.99 | 24.55 | 24.86 | 28.03 | 25.82
| 24 | 10.21 | 15.36 | 22.98 | 23.89 | 24.84 | 25.25
Note: Enter 8760 hourly data on sheet "TMPBIN" (next tab); the resulting bin data will flow to cells B330 through B478 here.
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA (Based on Hourly Integrated Values)
CASE 900FF
(USE COLUMN B ONLY)
| TEMP (°C) | # HOURS
| -50 | 0
| -49 | 0
| -48 | 0
| -47 | 0
| -46 | 0
| -45 | 0
| -44 | 0
| -43 | 0
| -42 | 0
| -41 | 0
| -40 | 0
| -39 | 0
| -38 | 0
| -37 | 0
| -36 | 0
| -35 | 0
| -34 | 0
| -33 | 0
| -32 | 0
| -31 | 0
| -30 | 0
| -29 | 0
| -28 | 0
| -27 | 0
| -26 | 0
| -25 | 0
| -24 | 0
| -23 | 0
| -22 | 0
| -21 | 0
| -20 | 0
| -19 | 0
| -18 | 0
| -17 | 0
| -16 | 0
| -15 | 0
| -14 | 0
| -13 | 0
| -12 | 0
| -11 | 0
| -10 | 0
| -9 | 0
| -8 | 0
| -7 | 0
| -6 | 0
| -5 | 0
| -4 | 0
| -3 | 0
| -2 | 0
| -1 | 0
| 0 | 0
| 1 | 4
| 2 | 4
| 3 | 20
| 4 | 21
| 5 | 39
| 6 | 51
| 7 | 63
| 8 | 71
| 9 | 83
| 10 | 128
| 11 | 164
| 12 | 218
| 13 | 185
| 14 | 197
| 15 | 253
| 16 | 269
| 17 | 241
| 18 | 312
| 19 | 321
| 20 | 337
| 21 | 305
| 22 | 324
| 23 | 302
| 24 | 276
| 25 | 296
| 26 | 283
| 27 | 313
| 28 | 302
| 29 | 326
| 30 | 356
| 31 | 386
| 32 | 366
| 33 | 399
| 34 | 374
| 35 | 315
| 36 | 253
| 37 | 209
| 38 | 152
| 39 | 118
| 40 | 64
| 41 | 34
| 42 | 17
| 43 | 7
| 44 | 2
| 45 | 0
| 46 | 0
| 47 | 0
| 48 | 0
| 49 | 0
| 50 | 0
| 51 | 0
| 52 | 0
| 53 | 0
| 54 | 0
| 55 | 0
| 56 | 0
| 57 | 0
| 58 | 0
| 59 | 0
| 60 | 0
| 61 | 0
| 62 | 0
| 63 | 0
| 64 | 0
| 65 | 0
| 66 | 0
| 67 | 0
| 68 | 0
| 69 | 0
| 70 | 0
| 71 | 0
| 72 | 0
| 73 | 0
| 74 | 0
| 75 | 0
| 76 | 0
| 77 | 0
| 78 | 0
| 79 | 0
| 80 | 0
| 81 | 0
| 82 | 0
| 83 | 0
| 84 | 0
| 85 | 0
| 86 | 0
| 87 | 0
| 88 | 0
| 89 | 0
| 90 | 0
| 91 | 0
| 92 | 0
| 93 | 0
| 94 | 0
| 95 | 0
| 96 | 0
| 97 | 0 |  | Sum (check)
| 98 | 0 |  | 8760