## A
Std140_CE_a_Output.xls
Output spreadsheet for HVAC BESTEST Cases CE100 through CE200
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Zone Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Zone Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
CE100 | 1541.2705 | 1328.6724 | 144.6674 | 67.9308 | 3799.9291 | 3799.9394 | 0 | 3655.2617 | 3655.272 | 0 | 2.3716 | 22.2 | 0.0077006 | 2.3718 | 22.2 | 0.0077006 | 2.3714 | 22.2 | 0.0077006
CE110 | 1084.7852 | 896.1989 | 128.328 | 60.2584 | 3764.7108 | 3764.7318 | 0 | 3636.3829 | 3636.4039 | 0 | 3.3522 | 22.2 | 0.0067292 | 3.3524 | 22.2 | 0.0067292 | 3.352 | 22.2 | 0.0067292
CE120 | 1021.8699 | 848.7411 | 117.8095 | 55.3193 | 3749.0776 | 3749.0776 | 0 | 3631.268 | 3631.268 | 0 | 3.5536 | 26.7 | 0.0080146 | 3.5538 | 26.7 | 0.0080146 | 3.5534 | 26.7 | 0.0080146
CE130 | 110.975 | 95.6675 | 10.4163 | 4.8912 | 218.3283 | 218.3283 | 2.0954e-13 | 207.912 | 207.912 | 2.0954e-13 | 1.8735 | 22.2 | 0.0077006 | 1.8739 | 22.2 | 0.0077006 | 1.8731 | 22.2 | 0.0077006
CE140 | 69.3257 | 57.2737 | 8.2011 | 3.851 | 197.2449 | 197.2449 | 3.5103e-13 | 189.0439 | 189.0439 | 3.5103e-13 | 2.7269 | 22.2 | 0.0067293 | 2.7275 | 22.2 | 0.0067293 | 2.7263 | 22.2 | 0.0067293
CE150 | 1215.47 | 1007.268 | 141.6759 | 66.5261 | 4517.2798 | 3778.0798 | 739.2 | 4375.6039 | 3636.4039 | 739.2 | 3.5999 | 22.2 | 0.008482 | 3.6001 | 22.2 | 0.0084824 | 3.5998 | 22.2 | 0.0084814
CE160 | 1148.25 | 957.5028 | 129.7984 | 60.9488 | 4500.2664 | 3761.0664 | 739.2 | 4370.468 | 3631.268 | 739.2 | 3.8062 | 26.7 | 0.010224 | 3.8064 | 26.7 | 0.010224 | 3.8061 | 26.7 | 0.010223
CE165 | 1511.0287 | 1290.5535 | 150.0275 | 70.4477 | 4537.0275 | 3797.8274 | 739.2001 | 4387 | 3647.7999 | 739.2001 | 2.9033 | 23.3 | 0.0095153 | 2.9038 | 23.3 | 0.0095184 | 2.9029 | 23.3 | 0.0095123
CE170 | 645.9497 | 537.2209 | 73.9871 | 34.7418 | 2231.991 | 1492.7909 | 739.2 | 2158.0039 | 1418.8039 | 739.2 | 3.3408 | 22.2 | 0.010631 | 3.3409 | 22.2 | 0.010633 | 3.3407 | 22.2 | 0.010628
CE180 | 1085.2728 | 910.5956 | 118.8632 | 55.814 | 4449.3139 | 1537.667 | 2911.6469 | 4330.4508 | 1418.8039 | 2911.6469 | 3.9902 | 22.2 | 0.016879 | 3.9908 | 22.2 | 0.016879 | 3.9897 | 22.2 | 0.016879
CE185 | 1561.4468 | 1354.4269 | 140.8715 | 66.1484 | 4535.3436 | 1578.5435 | 2956.8001 | 4394.4721 | 1437.672 | 2956.8001 | 2.8144 | 22.2 | 0.016076 | 2.8144 | 22.2 | 0.016079 | 2.8143 | 22.2 | 0.016073
CE190 | 166.8845 | 139.9663 | 18.3171 | 8.6011 | 576.9612 | 207.3609 | 369.6003 | 558.6441 | 189.0438 | 369.6003 | 3.3475 | 22.2 | 0.015848 | 3.349 | 22.2 | 0.015871 | 3.3461 | 22.2 | 0.015818
CE195 | 255.0302 | 221.1394 | 23.0618 | 10.8291 | 600.574 | 230.9737 | 369.6002 | 577.5122 | 207.912 | 369.6002 | 2.2645 | 22.2 | 0.015428 | 2.2655 | 22.2 | 0.015448 | 2.2636 | 22.2 | 0.015404
CE200 | 1481.7085 | 1254.5725 | 154.56 | 72.576 | 5497.0155 | 4275.9915 | 1221.024 | 5342.4555 | 4121.4315 | 1221.024 | 3.6056 | 26.7 | 0.011392 | 3.6065 | 26.7 | 0.011392 | 3.6049 | 26.7 | 0.011391