## A
Std140_CE_b_Output.xls
Output spreadsheet for HVAC BESTEST, Cases CE300 through CE545
INSTRUCTIONS
1. Use specified units.
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, CE300 Only
| B89..L112: |  | June 28 Hourly Output, Case CE300
| B120..L121: |  | Case CE500 Average Daily Outputs
| B129..L130: |  | Case CE530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima, Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case CE300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima, COP2 and Zone
3. Annual totals are consumption and/or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values that occur for the entire annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in Section 3.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24-hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 P.M.), shall
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | CE300 Only, Maxima
CE300 Only
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
CE300 | 35119.8488 | 21899.9807 | 2339.9481 | 10879.92 | 78195.153 | 55309.3775 | 22885.7755 | 3.294 | 23.4563 | 0.0094656 | 50.7998 | 19.9145 | 0.011608 | CE300 | 11379.6899 | 20-Jul | 15 | 23226.8644 | 20-Jul | 15 | 9582.8007 | 3-Sep | 15 | 31402.2464 | 15-Aug | 15 | 34.7 | 20-Jul | 15 | 0.021732 | 2-Oct | 9
CE310 | 39586.3028 | 25994.0514 | 2712.3314 | 10879.92 | 97553.0072 | 55289.6566 | 42263.3506 | 3.43 | 23.461 | 0.011249 | 59.8916 |  |  | CE310 | 12404.7707 | 20-Jul | 15 | 23052.6788 | 29-Jul | 15 | 15617.6044 | 3-Sep | 15 | 36897.1446 | 3-Sep | 15
CE320 | 39666.1039 | 26089.5074 | 2696.6765 | 10879.92 | 98302.4744 | 62065.9983 | 36236.4762 | 3.3887 | 24.3292 | 0.010011 | 51.004 |  |  | CE320 | 13062.4949 | 20-Jul | 15 | 31073.0735 | 24-Apr | 16 | 22699.7882 | 2-Oct | 10 | 40405.5525 | 3-Sep | 16
CE330 | 40600.0802 | 26988.4151 | 2731.7451 | 10879.92 | 103989.3084 | 62488.1983 | 41501.1101 | 3.4127 | 24.0486 | 0.010517 | 53.2975 |  |  | CE330 | 13759.2053 | 20-Jul | 15 | 32838.8404 | 24-Apr | 16 | 27826.537 | 18-Sep | 16 | 43663.3558 | 2-Oct | 9
CE340 | 40285.94 | 26674.4428 | 2731.5772 | 10879.92 | 101648.6078 | 62386.1243 | 39262.4835 | 3.3964 | 23.8158 | 0.010254 | 53.0681 |  |  | CE340 | 13351.8219 | 20-Jul | 15 | 32327.8556 | 24-Apr | 16 | 24664.9906 | 2-Oct | 10 | 41651.8032 | 2-Oct | 10
CE350 | 31801.0514 | 18930.9503 | 1990.1811 | 10879.92 | 67545.177 | 49123.4534 | 18421.7236 | 3.3175 | 25.3067 | 0.0099921 | 47.5302 |  |  | CE350 | 11379.6899 | 20-Jul | 15 | 23226.8644 | 20-Jul | 15 | 9582.8007 | 3-Sep | 15 | 31402.2464 | 15-Aug | 15
CE360 | 55141.0245 | 39969.3298 | 4291.7746 | 10879.92 | 162338.161 | 134720.3569 | 27617.8041 | 3.5766 | 24.6984 | 0.0088782 | 44.2372 |  |  | CE360 | 12791.4174 | 20-Jul | 15 | 31886.1205 | 24-Apr | 17 | 9031.1886 | 2-Oct | 10 | 38793.6036 | 2-Oct | 10
CE400 | 31851.6848 | 19006.5921 | 1965.1727 | 10879.92 | 67976.2378 | 42381.0041 | 25595.2337 | 3.2625 | 22.3988 | 0.010423 | 59.7287 |  |  | CE400 | 11655.3969 | 18-Sep | 16 | 23209.1571 | 20-Jul | 15 | 27826.537 | 18-Sep | 16 | 41945.2667 | 18-Sep | 16
CE410 | 33597.0955 | 20546.662 | 2170.5135 | 10879.92 | 72982.4596 | 51108.8433 | 21873.6163 | 3.2531 | 22.8748 | 0.0095591 | 53.2556 |  |  | CE410 | 11361.1306 | 20-Jul | 15 | 23209.1571 | 20-Jul | 15 | 9559.707 | 3-Sep | 15 | 31361.9226 | 15-Aug | 15
CE420 | 33387.1468 | 20360.5082 | 2146.7186 | 10879.92 | 72169.9235 | 50475.162 | 21694.7615 | 3.2511 | 22.8332 | 0.0096095 | 53.7578 |  |  | CE420 | 11361.1306 | 20-Jul | 15 | 23209.1571 | 20-Jul | 15 | 9559.707 | 3-Sep | 15 | 31361.9226 | 15-Aug | 15
CE430 | 32608.1434 | 19662.3245 | 2065.899 | 10879.92 | 69576.4422 | 48310.1099 | 21266.3323 | 3.2411 | 22.713 | 0.009651 | 54.3635 |  |  | CE430 | 11361.1306 | 20-Jul | 15 | 23209.1571 | 20-Jul | 15 | 9559.707 | 3-Sep | 15 | 31361.9226 | 15-Aug | 15
CE440 | 33515.3974 | 20473.7105 | 2161.7669 | 10879.92 | 72678.9008 | 50692.8945 | 21986.0063 | 3.251 | 22.8905 | 0.0095284 | 52.9602 |  |  | CE440 | 11361.1306 | 20-Jul | 15 | 23209.1571 | 20-Jul | 15 | 9559.707 | 3-Sep | 15 | 31361.9226 | 15-Aug | 15
CE500 | 23250.8759 | 18594.9753 | 1993.582 | 2662.3186 | 65815.0928 | 47492.3102 | 18322.7827 | 3.2209 | 20.8759 | 0.010203 | 68.9053 |  |  | CE500 | 10418.9052 | 20-Jul | 15 | 19834.8324 | 20-Jul | 16 | 7977.5075 | 20-Jul | 16 | 27812.3399 | 20-Jul | 16
CE500 May-Sep | 18163.9763 | 14569.9092 | 1538.9023 | 2055.1648 | 50530.4851 | 36470.5863 | 14059.8987 | 3.157 | 25 | 0.010895 | 55.0436 |  |  | CE510 | 11437.3255 | 20-Jul | 15 | 22282.1697 | 20-Jul | 16 | 8957.9663 | 20-Jul | 16 | 31240.136 | 20-Jul | 16
CE510 May-Sep | 36012.927 | 28828.2665 | 3076.2736 | 4108.387 | 113166.3461 | 81546.1854 | 31620.1607 | 3.5677 | 25 | 0.010915 | 55.1397 |  |  | CE520 | 11149.4313 | 16-Aug | 16 | 20412.3586 | 30-Jun | 16 | 7896.1877 | 30-Jun | 15 | 27774.3104 | 1-Jun | 16
CE520 | 26291.7844 | 20561.5481 | 2453.6285 | 3276.6079 | 66531.3713 | 48223.8303 | 18307.5411 | 2.8874 | 13.9797 | 0.0068018 | 69.3026 |  |  | CE522 | 10553.656 | 20-Jul | 15 | 19865.2971 | 20-Jul | 15 | 7776.5286 | 29-Jun | 16 | 27601.4598 | 29-Jun | 16
CE522 | 23567.004 | 18806.362 | 2038.4226 | 2722.2194 | 65932.5489 | 47597.0172 | 18335.5317 | 3.1839 | 17.4961 | 0.010915 | 86.9664 |  |  | CE525 | 9841.6513 | 20-Jul | 15 | 19641.811 | 20-Jul | 15 | 7842.919 | 29-Jun | 16 | 27453.986 | 29-Jun | 16
CE525 | 21008.269 | 17137.3228 | 1657.4804 | 2213.4657 | 65270.5916 | 46928.9814 | 18341.6102 | 3.5121 | 27.4973 | 0.013879 | 63.5565 |  |  | CE530 | 7952.5559 | 20-Jul | 15 | 19633.6518 | 20-Jul | 15 | 954.9839 | 11-Mar | 10 | 19633.6518 | 20-Jul | 15
CE530 | 17180.6707 | 13596.0195 | 1534.8903 | 2049.7609 | 46934.6038 | 46927.1087 | 7.4951 | 3.1369 | 20.8759 | 0.002058 | 20.8782 |  |  | CE540 | 9198.7841 | 20-Jul | 15 | 19867.9955 | 20-Jul | 15 | 1248.2378 | 11-Mar | 10 | 19868.112 | 20-Jul | 15
CE540 | 19520.5061 | 15109.5896 | 1888.6882 | 2522.2282 | 47514.4261 | 47506.1512 | 8.2749 | 2.8187 | 13.9551 | 0.0017769 | 20.6603 |  |  | CE545 | 8717.4354 | 20-Jul | 15 | 19599.1888 | 20-Jul | 15 | 3977.0111 | 20-Jul | 15 | 23576.1999 | 20-Jul | 15
CE545 | 11570.504 | 9187.6077 | 1020.2704 | 1362.6259 | 46192.4585 | 46137.7033 | 54.7552 | 4.7525 | 27.4974 | 0.0018472 | 18.9956
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e C E 3 0 0 | [13 empty] | A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor | [5 empty] | C O P 2 |  |  |  |  | Indoor Drybulb Temperature | [5 empty] | Humidity Ratio | [5 empty] | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  | Cases |  | Maximum |  |  | Minimum |  |  | Maximum |  |  | Minimum* |  |  | Maximum |  |  | Minimum* |  |  | Maximum* |  |  | Minimum*
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 1969.2842 | 244.7842 | 7759.0472 | 5926.1857 | 1832.8615 | 0.0094461 | 3.5044 | 18.05 | 23.9603 | 17.1775 | 0.011245 |  |  | CE300 | 3.9118 | 1-Jan | 1 | 2.7711 | 13-Jun | 17 | 26.4672 | 20-Jul | 15 | 5.6117 | 6-Jan | 6 | 0.014757 | 10-Jul | 12 | 0.0018936 | 11-Jan | 3 | 70.3493 | 16-Nov | 17 | 14.878 | 6-Nov | 5
2 | 1953.797 | 242.9408 | 7689.1998 | 5894.2621 | 1794.9376 | 0.009395 | 3.5003 | 18.05 | 23.9483 | 17.1307 | 0.011251 |  |  | CE310 | 4.171 | 30-Apr | 15 | 2.8604 | 1-Dec | 15 | 26.9182 | 20-Jul | 15 | 5.6117 | 6-Jan | 6 | 0.017089 | 10-Jul | 13 | 0.0018937 | 11-Jan | 3 | 79.5199 | 10-Jul | 12 | 14.8964 | 6-Nov | 5
3 | 1966.7548 | 244.5001 | 7746.6084 | 5924.6509 | 1821.9575 | 0.0094287 | 3.5033 | 18.05 | 23.9597 | 17.1628 | 0.011245 |  |  | CE320 | 3.9722 | 1-Jan | 1 | 2.8222 | 31-Mar | 15 | 32.248 | 20-Jul | 15 | 7.9165 | 6-Jan | 6 | 0.018012 | 1-Oct | 10 | 0.0018933 | 11-Jan | 3 | 82.5464 | 18-Sep | 10 | 13.4149 | 6-Nov | 5
4 | 1918.1601 | 239.6613 | 7579.9259 | 5825.5626 | 1754.3632 | 0.0093543 | 3.5128 | 17.8 | 23.9169 | 17.0857 | 0.01106 |  |  | CE330 | 4.0778 | 16-Sep | 14 | 2.8337 | 31-Mar | 15 | 34.7 | 20-Jul | 15 | 5.6117 | 6-Jan | 6 | 0.021804 | 2-Oct | 9 | 0.0018936 | 11-Jan | 3 | 98.5067 | 30-Apr | 9 | 14.878 | 6-Nov | 5
5 | 1852.7502 | 233.0651 | 7337.9298 | 5726.0612 | 1611.8687 | 0.0091688 | 3.518 | 17.5 | 23.873 | 16.9145 | 0.010598 |  |  | CE340 | 4.0087 | 16-Sep | 15 | 2.8337 | 31-Mar | 15 | 33.3703 | 20-Jul | 15 | 5.6117 | 6-Jan | 6 | 0.019485 | 2-Oct | 10 | 0.0018936 | 11-Jan | 3 | 87.3492 | 22-Sep | 20 | 14.878 | 6-Nov | 5
6 | 1937.2392 | 240.5765 | 7521.3894 | 5994.7169 | 1526.6725 | 0.0089733 | 3.4536 | 18.3 | 23.9921 | 16.791 | 0.010547 |  |  | CE350 | 3.9306 | 5-Oct | 1 | 2.7711 | 13-Jun | 17 | 33.9838 | 25-Jun | 7 | 5.6117 | 6-Jan | 6 | 0.016973 | 1-Oct | 24 | 0.0018936 | 11-Jan | 3 | 70.3493 | 16-Nov | 17 | 14.878 | 6-Nov | 5
7 | 2589.4978 | 298.0625 | 9375.3512 | 7314.1767 | 2061.1745 | 0.0095468 | 3.2468 | 22.2 | 24.5782 | 17.4711 | 0.012022 |  |  | CE360 | 4.4022 | 5-Oct | 1 | 2.8337 | 31-Mar | 15 | 33.3879 | 10-Jul | 13 | 5.6117 | 6-Jan | 6 | 0.014105 | 10-Jul | 13 | 0.0018936 | 11-Jan | 3 | 70.3493 | 16-Nov | 17 | 14.878 | 6-Nov | 5
8 | 3260.9071 | 350.7391 | 10995.1998 | 8630.5874 | 2364.6124 | 0.0098901 | 3.0444 | 26.1 | 25.1656 | 17.952 | 0.012109 |  |  | CE400 | 4.072 | 16-Sep | 14 | 2.7709 | 13-Jun | 17 | 26.5095 | 20-Jul | 15 | 5.6117 | 6-Jan | 6 | 0.019191 | 18-Sep | 16 | 0.0018936 | 11-Jan | 3 | 100 | 22-Apr | 6 | 15.0947 | 6-Nov | 6
9 | 4358.6625 | 455.2329 | 14461.446 | 11631.1622 | 2830.2838 | 0.0098025 | 3.0041 | 28.05 | 25.4589 | 17.9792 | 0.011466 |  |  | CE410 | 3.8827 | 30-Apr | 15 | 2.7709 | 13-Jun | 17 | 26.5095 | 20-Jul | 15 | 5.6117 | 6-Jan | 6 | 0.014862 | 2-Apr | 2 | 0.0018936 | 11-Jan | 3 | 87.1608 | 2-Apr | 2 | 15.0947 | 6-Nov | 6
10 | 4618.6153 | 474.1516 | 15187.1427 | 11915.6348 | 3271.5079 | 0.010283 | 2.9821 | 28.9 | 25.5872 | 18.4074 | 0.012309 |  |  | CE420 | 3.7302 | 27-Sep | 16 | 2.7709 | 13-Jun | 17 | 26.5095 | 20-Jul | 15 | 5.6117 | 6-Jan | 6 | 0.014783 | 10-Jul | 12 | 0.0018936 | 11-Jan | 3 | 87 | 21-May | 14 | 15.0947 | 6-Nov | 6
11 | 4977.6515 | 499.6118 | 16184.5736 | 12284.3523 | 3900.2214 | 0.010853 | 2.9549 | 30 | 25.754 | 18.9097 | 0.013692 |  |  | CE430 | 3.7867 | 24-Oct | 15 | 2.7709 | 13-Jun | 17 | 26.5095 | 20-Jul | 15 | 5.6117 | 6-Jan | 6 | 0.016175 | 2-Apr | 5 | 0.0018936 | 11-Jan | 3 | 96.5764 | 24-Oct | 13 | 15.0947 | 6-Nov | 6
12 | 5225.5654 | 516.3428 | 16808.1967 | 12570.3933 | 4237.8034 | 0.011238 | 2.9273 | 30.85 | 25.883 | 19.2499 | 0.013953 |  |  | CE440 | 3.7697 | 21-May | 15 | 2.7709 | 13-Jun | 17 | 27.8588 | 24-Apr | 17 | 5.6117 | 6-Jan | 6 | 0.014783 | 10-Jul | 12 | 0.0018936 | 11-Jan | 3 | 82.9585 | 30-Apr | 10 | 15.0947 | 6-Nov | 6
13 | 6469.8987 | 646.014 | 21368.9567 | 17260.1196 | 4108.8371 | 0.010157 | 3.003 | 30.85 | 25.8809 | 18.4029 | 0.012238 |  |  | CE500 | 4.1921 | 16-Mar | 10 | 2.6948 | 30-Jul | 12 | 25 | 26-Mar | 14 | 7.5279 | 20-Dec | 13 | 0.012154 | 20-Jul | 15 | 0.0064426 | 20-Dec | 13 | 100 | 5-Jan | 7 | 50.164 | 1-Jan | 1
14 | 6403.5669 | 637.199 | 20741.0942 | 17430.9212 | 3310.173 | 0.0096128 | 2.9459 | 31.4 | 25.9582 | 17.9935 | 0.011476 |  |  | CE510 | 4.6843 | 5-Oct | 1 | 2.8907 | 31-Mar | 15 | 25 | 26-Mar | 14 | 7.5279 | 20-Dec | 13 | 0.012191 | 20-Jul | 15 | 0.0064426 | 20-Dec | 13 | 100 | 5-Jan | 7 | 50.164 | 1-Jan | 1
15 | 7878.1699 | 778.2372 | 26275.3387 | 22315.3008 | 3960.0378 | 0.009523 | 3.0354 | 31.95 | 26.0451 | 17.9499 | 0.012004 |  |  | CE520 | 3.8265 | 1-Jan | 1 | 2.4251 | 31-Mar | 17 | 17.2385 | 16-Aug | 16 | 7.5061 | 20-Dec | 13 | 0.0080896 | 1-Jan | 1 | 0.0048546 | 29-Jul | 14 | 100 | 4-Jan | 20 | 43.7796 | 20-Jul | 15
16 | 8045.9061 | 789.7297 | 26856.7831 | 22407.3576 | 4449.4255 | 0.0099081 | 3.0396 | 32.2 | 26.0866 | 18.2733 | 0.013259 |  |  | CE522 | 4.1349 | 30-Apr | 15 | 2.6732 | 8-Jul | 17 | 20.1766 | 1-Jan | 1 | 7.5275 | 20-Dec | 13 | 0.012331 | 20-Jul | 15 | 0.0064424 | 20-Dec | 13 | 100 | 4-Jan | 21 | 63.2928 | 1-Jan | 1
17 | 5359.6242 | 522.3546 | 16815.8055 | 12936.4532 | 3879.3523 | 0.011176 | 2.8589 | 31.95 | 26.0487 | 19.2541 | 0.014442 |  |  | CE525 | 4.655 | 16-Mar | 10 | 2.8753 | 8-Jul | 17 | 35 | 8-May | 12 | 7.5288 | 20-Dec | 13 | 0.016956 | 20-Jul | 16 | 0.006443 | 20-Dec | 13 | 100 | 5-Jan | 7 | 42.2392 | 11-Mar | 11
18 | 5433.3639 | 530.7578 | 17397.5825 | 12749.6179 | 4647.9646 | 0.011716 | 2.917 | 31.4 | 25.966 | 19.6405 | 0.015169 |  |  | CE530 | 4.0713 | 16-Mar | 10 | 2.6085 | 8-Jul | 17 | 25 | 12-Mar | 16 | 7.5279 | 20-Dec | 13 | 0.009881 | 1-Jan | 5 | 0.00037042 | 30-Apr | 23 | 100 | 5-Jan | 7 | 1.9031 | 30-Apr | 23
19 | 5180.2559 | 517.7568 | 17194.6996 | 12179.9648 | 5014.7348 | 0.011634 | 3.0177 | 29.7 | 25.7094 | 19.497 | 0.015072 |  |  | CE540 | 3.8265 | 1-Jan | 1 | 2.276 | 8-Jul | 17 | 15.417 | 1-Jan | 1 | 7.5061 | 20-Dec | 13 | 0.0080896 | 1-Jan | 1 | 0.00037984 | 0-May | 24 | 100 | 4-Jan | 20 | 3.6263 | 0-May | 24
20 | 4840.3561 | 498.1719 | 16706.6126 | 11531.186 | 5175.4266 | 0.011607 | 3.1294 | 27.75 | 25.4176 | 19.3844 | 0.015682 |  |  | CE545 | 6.6673 | 5-Oct | 1 | 2.7339 | 8-Jul | 17 | 35 | 18-Mar | 11 | 7.5288 | 20-Dec | 13 | 0.009881 | 1-Jan | 5 | 0 | 4-Jun | 15 | 100 | 5-Jan | 7 | 0 | 4-Jun | 15
21 | 3967.4585 | 410.0329 | 13594.3683 | 8996.4847 | 4597.8835 | 0.012012 | 3.1055 | 27.2 | 25.3329 | 19.6656 | 0.016809 |  |  | * Note: For Cases CE500-CE545 only, the following results are extracted from the period April 1 - Dec 31 (using a full annual simulation): minimum IDB, minimum zone humidity ratio, maximum and minimum relative humidity.
22 | 3927.799 | 407.5333 | 13526.6775 | 8925.6485 | 4601.029 | 0.012018 | 3.1201 | 26.95 | 25.3011 | 19.66 | 0.016778
23 | 3829.166 | 400.7913 | 13329.5505 | 8743.6458 | 4585.9048 | 0.012019 | 3.1512 | 26.4 | 25.2193 | 19.6353 | 0.016776
24 | 3789.5551 | 398.2297 | 13285.2798 | 8626.5366 | 4658.7432 | 0.012093 | 3.1724 | 26.1 | 25.1668 | 19.6745 | 0.017021
C a s e C E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 4051.9712 | 3135.0782 | 392.6113 | 524.2817 | 13704.5266 | 9881.8643 | 3822.6623 | 0.01052 | 3.8438 | 16.7917 | 25
June 25 | 5275.1783 | 4272.6917 | 429.2487 | 573.2378 | 13779.5777 | 9951.3745 | 3828.2031 | 0.011096 | 2.9279 | 29.5167 | 25
C a s e C E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 2990.1605 | 2288.4296 | 300.4808 | 401.2501 | 9769.0213 | 9767.9271 | 1.0942 | 0.00037944 | 3.7423 | 16.7917 | 25
June 25 | 3908.8812 | 3134.1745 | 331.7095 | 442.9972 | 9832.026 | 9831.6323 | 0.39363 | 0.00046837 | 2.8448 | 29.5167 | 25